## ID_385217 (4)
DEVICE_TYPE | ABBREVIATION | UNIT | DESCRIPTION
meteo | E_LIGHTNING_COUNT |  | Lightning events interval
meteo | E_LIGHTNING_COUNT_TOTAL |  | Lightning events total
battery | B_I_DIS_DC | A | Discharging current DC
meter | M_EQ_IND_INT_IMP | kVArh | Reactive energy imported inductively per interval
meter | M_EQ_CAP_INT_IMP | kVArh | Reactive energy imported capacitively per interval
power-plant-controller | PPC_P_SET_STATIC_REL | % | Relative active power setpoint (static)
power-plant-controller | PPC_P_SET_STATIC_ABS | W | Absolute active power setpoint (static)
meteo | E_DEWPOINT | °C | Dewpoint
power-plant-controller | PPC_P_SET_MANUAL_ABS | W | Absolute active power setpoint (manually)
power-plant-controller | PPC_P_SET_MANUAL_REL | % | Relative active power setpoint (manually)
power-plant-controller | PPC_P_SET_ABS | W | Absolute active power setpoint
power-plant-controller | PPC_P_SET_RPC_ABS | W | Absolute active power setpoint (3rd party)
battery | B_E_INT_IMP_AC | kWh | Energy import from storage system (interval) AC
battery | B_E_INT_EXP_AC | kWh | Energy export from storage system (interval) AC
battery | B_U_CELL([1-9][0-9]{0,2}(_[1-9][0-9]{0,2}){0,2})?$ | V | Cell voltage
battery | B_U_CELL_MAX([1-9][0-9]{0,2})(_[1-9][0-9]{0,2})?$ | V | Maximum cell voltage
battery | B_U_CELL_MIN([1-9][0-9]{0,2})(_[1-9][0-9]{0,2})?$ | V | Minimum cell voltage
battery | B_U_CELL_AVG | V | Average cell voltage
battery | B_T_CELL_MAX([1-9][0-9]{0,2})(_[1-9][0-9]{0,2})?$ | °C | Maximum cell temperature [°C]
battery | B_T_CELL_MIN([1-9][0-9]{0,2})(_[1-9][0-9]{0,2})?$ | °C | Minimum cell temperature [°C]
battery | B_T_CELL([1-9][0-9]{0,2}(_[1-9][0-9]{0,2}){0,2})?$ | °C | Cell temperature [°C]
battery | B_T_M_MIN([1-9][0-9]{0,2})?$ | °C | Minimum module temperature [°C]
battery | B_T_M_MAX([1-9][0-9]{0,2})?$ | °C | Maximum module temperature [°C]
battery | B_S_AC | VA | Battery apparent power AC
battery | B_Q_AC | VAr | Battery reactive power AC
battery | B_P_AC | W | Battery power AC
battery | B_F_AC | Hz | Grid frequency
battery | B_I_AC | A | Battery AC current
battery | B_U_AC | V | Battery AC voltage
battery | B_E_DISCHARGE_AC | kWh | Dischargeable Energy
battery | B_E_CHARGE_AC | kWh | Chargeable Energy
battery | B_LIM_U_CHARGE | V | Charge end voltage
battery | B_LIM_P_DISCHARGE | W | Maximum discharging power
battery | B_LIM_P_CHARGE | W | Maximum charging power
battery | B_E_IMP_AC | kWh | Energy import to storage system AC
battery | B_E_EXP_AC | kWh | Energy export from storage system AC
tracker | ACC_Z | m/s² | Sensor acceleration on vertical axis
tracker | ACC_Y | m/s² | Sensor acceleration on north-south axis
tracker | ACC_X | m/s² | Sensor acceleration on east-west axis
meter | M_AC_EQ_TOTAL | kVArh | kVAR-hours - Reactive Energy total
meteo | SR[1-9]{1}$ | % | Soiling ratio
meter | M_EQ_CAP_INT_EXP | kVArh | Reactive energy exported capacitively per interval
meter | M_EQ_IND_INT_EXP | kVArh | Reactive energy exported inductively per interval
power-plant-controller | PPC_P_SET_CTRL_REL | % | Relative active power correction value
genset | P_AC_SET_REL | % | Relative active power setpoint
genset | Q_AC_SET_ABS | VAr | Absolute reactive power setpoint
genset | P_AC_SET_ABS | W | Absolute active power setpoint
meteo | WATER_DEPTH | m | Water depth
inverter | U_DC_PE | V | Voltage DC positive pole to earth
inverter | U_DC_NE | V | Voltage DC negative pole to earth
tracker | T([1-9][0-9]{0,2})?$ | °C | Temperatures
meteo | E_RF_DIF([1-9][0-9]{0,2})?$ | mm | Differential precipitation
status | STATE([1-9][0-9]{0,2})?$ |  | Global device state
meteo | STATE([1-9][0-9]{0,2})?$
meter | STATE([1-9][0-9]{0,2})?$
battery | B_LIM_U_DISCHARGE |  | Discharge end voltage
battery | B_LIM_I_DISCHARGE |  | Maximum discharging current
battery | B_LIM_I_CHARGE |  | Maximum charging current
inverter | T([1-9][0-9]{0,2})?$ | °C | inverter temperatures
power-plant-controller | PPC_PF |  | Actual power factor
power-plant-controller | PPC_Q_AC | VAr | Actual reactive power
power-plant-controller | PPC_P_AC | W | Actual active power
power-plant-controller | PPC_P_AC_RPC_MAX | W | Maximum active power during curtailment (3rd party)
power-plant-controller | PPC_P_AC_GRIDOP_MAX | W | Maximum active power during curtailment (grid operator)
power-plant-controller | PPC_PF_SET |  | Power factor setpoint
power-plant-controller | PPC_Q_SET_ABS | VAr | Absolute reactive power setpoint
power-plant-controller | PPC_Q_SET_REL | % | Actual valid reactive power setpoint
power-plant-controller | PPC_P_SET_REL | % | Actual valid active power setpoint
power-plant-controller | PPC_P_SET_RPC_REL | % | Active power setpoint (3rd party)
power-plant-controller | PPC_P_SET_GRIDOP_ABS | W | Absolute active power setpoint (grid operator)
power-plant-controller | PPC_P_SET_GRIDOP_REL | % | Relative active power setpoint (grid operator)
power-plant-controller | PPC_Q_AC_AVAIL | VAr | Actual theoretical available reactive power
power-plant-controller | PPC_P_AC_AVAIL | W | Actual theoretical available active power
power-plant-controller | PPC_P_AC_INV | W | Sum of inverter actual active power
tracker | QS_RX |  | Telegrams received (communication quality)
tracker | QS_TX |  | Telegrams transmitted (communication quality)
battery | QS_RX |  | Telegrams received (communication quality)
battery | QS_TX |  | Telegrams transmitted (communication quality)
stringbox | QS_RX |  | Telegrams received (communication quality)
stringbox | QS_TX |  | Telegrams transmitted (communication quality)
meter | QS_RX |  | Telegrams received (communication quality)
meter | QS_TX |  | Telegrams transmitted (communication quality)
meteo | QS_RX |  | Telegrams received (communication quality)
meteo | QS_TX |  | Telegrams transmitted (communication quality)
inverter | QS_RX |  | Telegrams received (communication quality)
inverter | QS_TX |  | Telegrams transmitted (communication quality)
genset | QS_RX |  | Telegrams received (communication quality)
genset | QS_TX |  | Telegrams transmitted (communication quality)
tracker | ERROR([1-9][0-9]{0,2})?$ |  | Global tracker error conditions
tracker | STATE([1-9][0-9]{0,2})?$ |  | Global tracker state conditions
tracker | MODE |  | Mode of tracker (0 = Auto, follow programmed path, 1 = Manual, go to a fixed position, 2 = Storm, go to a fixed position, 3 = Calibrate, execute test mode, 4 = Clean, go to a fixed position)
tracker | AZIMUTH | ° | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
tracker | AZIMUTH_MANUAL | ° | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
tracker | AZIMUTH_TARGET | ° | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
tracker | ELEVATION | ° | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type
tracker | ELEVATION_MANUAL | ° | Global manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type
tracker | ELEVATION_TARGET | ° | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
tracker | TRACKER_TYPE |  | Type of tracker (0 = Unknown / Not Set, 1 = Fixed / Documented orientation information, 2 = Single Axis Horizontal, 3 = Single Axis Tilted Horizontal, 4 = Single Axis Azimuth, 5 = Dual Axis, 99 = Other type) **Deprecated**
battery | ERROR([1-9][0-9]{0,2})?$ |  | Global battery error conditions
battery | STATE([1-9][0-9]{0,2})?$ |  | Global battery state conditions
battery | T([1-9][0-9]{0,2})?$ | °C | Temperatures
stringbox | ERROR([1-9][0-9]{0,2})?$ |  | Global stringbox error conditions
stringbox | P_DC | W | DC-Power
genset | ERROR([1-9][0-9]{0,2})?$ |  | Global genset error conditions
genset | STATE([1-9][0-9]{0,2})?$ |  | Global inverter genset conditions
genset | I_AC([1-3])?$ | A | Current AC (single phase or accumulated)
genset | U_AC_L3L1 | V | Voltage phase 3-1
genset | U_AC_L2L3 | V | Voltage phase 2-3
genset | U_AC_L1L2 | V | Voltage phase 1-2
genset | U_AC([1-3])?$ | V | Voltage AC (single phase or accumulated)
genset | F_AC([1-3])?$ | Hz | Grid frequency (single phase or accumulated)
genset | COS_PHI |  | Power factor cos phi
genset | S_AC([1-3])?$ | VA | Total apparent power (single phase or accumulated)
genset | Q_AC([1-3])?$ | VAr | Total reactive power (single phase or accumulated)
genset | P_AC([1-3])?$ | W | Power AC (single phase or accumulated)
genset | E_INT | kWh | Yield in current interval
genset | E_TOTAL | kWh | Total yield
genset | OT_REMAINING | h | Operation hours remaining
genset | OT_TOTAL | h | Operation hours
genset | FUEL_EFFICIENCY | kWh/l | Fuel efficiency
genset | FUEL_REMAINING | % | Fuel remaining
genset | FUEL_CONSUMPTION | l/h | Fuel consumption
meteo | SNOW_LOAD([1-9][0-9]{0,2})?$ | kg/m² | Snow load
meteo | E_F_S([1-9][0-9]{0,2})?$ | rpm | Fan speed
meteo | E_TILT([1-9][0-9]{0,2})?$ | ° | Sensor Tilt (relative to horizontal)
meteo | E_IP_ABS([1-9][0-9]{0,2})?$ | hPa | Internal air pressure
meteo | E_IH_REL([1-9][0-9]{0,2})?$ | % | Internal relative humidity
inverter | I_DC([1-9][0-9]{0,2})_([1-9][0-9]{0,2})$ | A | Current DC (single string)
meteo | SUN_H([1-9][0-9]{0,2})?$ | h | Sunshine duration
battery | B_E_INT_EXP | kWh | Energy export from storage system (interval) DC
battery | B_E_INT_IMP | kWh | Energy import to storage system (interval) DC
meteo | SLI_RAW([1-9][0-9]{0,2})?$ | % | Soiling Loss Raw
meteo | SLI([1-9][0-9]{0,2})?$ | % | Soiling Loss
meteo | E_SNOW_DEPTH([1-9][0-9]{0,2})?$ | m | Snow depth
meter | M_DC_E_EXP | kWh | Active Energy DC (export)
meter | M_DC_E_IMP | kWh | Active Energy DC (import)
meter | M_DC_I([1-3])?$ | A | Current DC [Phase 1-3]
meter | M_DC_P([1-3])?$ | W | Power DC [Phase 1-3]
meter | M_DC_U([1-3])?$ | V | Voltage DC, Phase [1-3]
meter | M_AC_P([1-3])?$ | W | Active Power [Phase 1-3]
meteo | ERROR([1-9][0-9]{0,2})?$ |  | Global meteo error conditions
meter | ERROR([1-9][0-9]{0,2})?$ |  | Global meter error conditions
meteo | T([1-9][0-9]{0,2})?$ | °C | Temperature values
meteo | SRAD([1-9][0-9]{0,2})?$ | W/m2 | Irradiation sensors
battery | B_U_BULK | V | Battery charging voltage DC
battery | B_I_DC | A | Charging current DC
battery | B_U_DC | V | Battery voltage
battery | B_T_M([1-9][0-9]{0,2})(_[1-9][0-9]{0,2})?$ | °C | Module temperature [°C]
battery | B_SOCH | % | State of charge (nominal capacity)
battery | B_E_STORED | kWh | Currently stored energy
battery | B_SOH | % | State of health
battery | B_CAPACITY | Ah | Nominal capacity
meter | M_AC_OT_TOTAL | hour | Operation Time TOTAL
inverter | U_AC_L3L1 | V | Volts L3-L1
inverter | U_AC_L2L3 | V | Volts L2-L3
inverter | U_AC_L1L2 | V | Volts L1-L2
battery | B_E_EXP | kWh | Energy export from storage system DC
battery | B_E_IMP | kWh | Energy import to storage system DC
battery | B_OT_TOTAL | h | Operating Hours
battery | B_T_U([1-9][0-9]{0,2})?$ | °C | Temperature Outside/ Ambient [°C]
battery | B_SOC | % | State of Charge
battery | B_U_OC | V | Open circuit voltage
battery | B_P_DC | W | Total battery power
meter | M_AC_U_L3L1 | V | Volts L3-L1
meter | M_AC_U_L2L3 | V | Volts L2-L3
meter | M_AC_U_L1L2 | V | Volts L1-L2
meter | M_AC_U([1-3])?$ | V | Voltage, Phase [1-3]
meter | M_AC_S([1-3])?$ | VA | Apparent Power [Phase 1-3]
meter | M_AC_Q([1-3])?$ | VAr | Reactive Power [Phase 1-3]
meter | M_AC_PF_TANPHI | tanphi | Power Factor (tanphi)
meter | M_AC_PF_COSPHI([1-9][0-9]*)? | cosphi | Power Factor (cos(phi))
meter | M_AC_I_SF |  | CT Ratio (Scalefactor)
meter | M_AC_I_N | A | Neutral Current
meter | M_AC_I([1-3])?$ | A | Current [Phase 1-3]
meter | M_AC_F([1-9][0-9]*)? | Hz | Frequency
meter | M_AC_E_IMP([1-9][0-9]*)? | kWh | kW-hours, Imported
meter | M_AC_E_EXP([1-9][0-9]*)? | kWh | kW-hours, Exported
meter | M_AC_ES_IMP | kVAh | kVA-hours - Apparent Energy Imported
meter | M_AC_ES_EXP | kVAh | kVA-hours - Apparent Energy Exported
meter | M_AC_EQ_IND_IMP | kVArh | kVAR-hours, Positive - Reactive Energy inductive imported
meter | M_AC_EQ_IND_EXP | kVArh | kVAR-hours, Positive - Reactive Energy inductive exported
meter | M_AC_EQ_CAP_IMP | kVArh | kVAR-hours, Positive - Reactive Energy capacitive imported
meter | M_AC_EQ_CAP_EXP | kVArh | kVAR-hours, Negative - Reactive Energy capacitive exported
stringbox | U_DC | V | DC-Voltage
stringbox | T([1-9][0-9]{0,2})?$ | °C | Temperatures
stringbox | STATE([1-9][0-9]{0,2})?$ |  | Global strongbox state conditions
stringbox | I_SUM | A | Sum of all string values
stringbox | I_AVG | A | Average value of all string values
stringbox | I([1-9][0-9]{0,2})$ | A | Current value of string 1..x (`I` without number is not allowed)
stringbox | D_IN([1-9][0-9]{0,2})?$ |  | Digital input
stringbox | A_IN([1-9][0-9]{0,2})?$ |  | Optional analogue inputs
meteo | E_W_S([1-9][0-9]{0,2})?_MAX$ | m/s | Maximum wind speed
meteo | E_W_S([1-9][0-9]{0,2})?$ | m/s | Wind speed
meteo | E_W_D([1-9][0-9]{0,2})?$ | ° | Wind direction
meteo | E_RF_I([1-9][0-9]{0,2})?$ | mm/h | Precipitation intensity
meteo | E_RF_ABS([1-9][0-9]{0,2})?$ | mm | Absolute precipitation
meteo | E_PRECIPITATION |  | Type of precipitation (0 = None; 10 = Rain; 20 = Snow; 30 = Unspecified)
meteo | E_AT([1-9][0-9]{0,2})?$ | °C | Air temperature
meteo | E_AP_REL([1-9][0-9]{0,2})?$ | hPa | Relative air pressure
meteo | E_AP_ABS([1-9][0-9]{0,2})?$ | hPa | Absolute air pressure
meteo | E_ALT([1-9][0-9]{0,2})?$ | m | Local height
meteo | E_AH_REL([1-9][0-9]{0,2})?$ | % | Relative humidity
meteo | E_AH_ABS([1-9][0-9]{0,2})?$ | g/m³ | Absolute humidity
inverter | U_DC([1-9][0-9]{0,2})?$ | V | Voltage DC (single input or accumulated)
inverter | U_AC([1-3])?$ | V | Voltage AC (single phase or accumulated)
inverter | T_WR([1-9][0-9]{0,2})?$ | °C | inverter temperatures
inverter | S_AC([1-3])?$ | VA | Apparent power (single phase or accumulated)
inverter | STATE([1-9][0-9]{0,2})?$ |  | Global inverter state conditions
inverter | R_ISO | kOhm | Isolation resistant
inverter | R_AC | mOhm | Grid impedance
inverter | Q_AC([1-3])?$ | VAr | Reactive power (single phase or accumulated)
inverter | P_DC([1-9][0-9]{0,2})?$ | W | Power DC (single input or accumulated)
inverter | P_AC([1-3])?$ | W | Power AC (single phase or accumulated)
inverter | OT_AC_TOTAL | hour | Operation Time TOTAL
inverter | OT_AC_DAY | min | Operation Time DAY
inverter | I_GDFI | mA | Earth leakage current
inverter | I_DC([1-9][0-9]{0,2})?$ | A | Current DC (single input or accumulated)
inverter | I_AC[1-9]{0,1}$ | A | Current AC (single phase or accumulated)
inverter | F_AC[1-9]{0,1}$ | Hz | Grid frequency (single phase or accumulated)
inverter | FT_AC_TOTAL | hour | Feed in Time Total AC
inverter | FT_AC_DAY | min | Feed in Time Day AC
inverter | E_YEAR | kWh | Energy generated per year
inverter | E_TOTAL | kWh | Total generated energy
inverter | E_INT | kWh | Energy generated per interval
inverter | E_DAY | kWh | Energy generated per day
inverter | ERROR([1-9][0-9]{0,2})?$ |  | Global inverter error conditions
inverter | D_IN([1-9][0-9]{0,2})?$ |  | Digital input
inverter | COS_PHI_NOM([1-3])?$ |  | Cos Phi given value
inverter | COS_PHI_LOAD([1-3])?$ |  | Inductive or capacitive load (c/i)
inverter | COS_PHI |  | Cos Phi actual value
inverter | A_IN([1-9][0-9]{0,2})?$ |  | Analogue input
calculated | AREA | m² | module area plant
calculated | POWER | kW | nominal power plant
calculated | E_GM | Wh/m2 | Radiation energy
calculated | E_MESS |  | Energy measured
calculated | PR | % | performance ratio plant
calculated | E_ZAEHLER |  | Energy over meter
calculated | E_N |  | Specific yield
calculated | EPI | % | Energy Performance Index
calculated | CO2 | t | Saved CO2
calculated | VFG | % | System availability
calculated | G_M0 | W/m2 | irradiance sensor plant
calculated | E_Z_EVU | kWH | interal energy plant